SURVEY 713 CES-ENV-27-014

Wall-system asbestos survey

Mother Base Community Support Center · Building 620 · Final signed record

| INSPECTION DATES | 11–13 May 2027 |
| --- | --- |
| REPORT DATE | 18 May 2027 |
| SURVEY SCOPE | All identified accessible interior and exterior wall-system types |
| LABORATORY | Arctic Analytical Services · Exercise Laboratory AAS-027 |
| METHOD | Bulk sampling and polarized-light microscopy; asbestos reported at less than 1 percent as negative |

SURVEY RECORD

| SAMPLES | WALL-SYSTEM AREA | TESTED | POSITIVE | RESULT |
| --- | --- | --- | --- | --- |
| W-01–03 | Administrative-suite gypsum systems | 3 | 0 | NEGATIVE |
| W-04–06 | Activity and recreation-room systems | 3 | 0 | NEGATIVE |
| W-07–09 | Multipurpose-hall wall systems | 3 | 0 | NEGATIVE |
| W-10–12 | Kitchen and dining wall systems | 3 | 0 | NEGATIVE |
| W-13–15 | Service, storage, and utility systems | 3 | 0 | NEGATIVE |
| W-16–18 | Perimeter wall finishes and coatings | 3 | 0 | NEGATIVE |
| TOTAL WALL-SYSTEM SAMPLES |  | 18 | 0 | ALL NEGATIVE |

SURVEY CONCLUSION. All wall-system samples tested negative. No asbestos-containing material was identified in the Community Support Center wall systems included in this survey.

LIMITATION. This record addresses wall systems only. It does not clear roofing, flooring, mechanical insulation, equipment, underground materials, or inaccessible non-wall components.

| /s/ NAOMI HUNTER NAOMI HUNTER, GS-12, DAF Certified Asbestos Inspector · 713 CES/CEIE Signed 18 May 2027 | /s/ HAL EMMERICH HAL EMMERICH, NH-03, DAF Chief Facilities Engineer · 713 CES/CEN CES concurrence · 18 May 2027 |
| --- | --- |