713TH CIVIL ENGINEER SQUADRON

# INSTALLATION PHOTOGRAPH AND GOVERNMENT USE RECORD

Campbell Hall Office 214

Photograph 1. Office 214 indoor unit on 14 August 2027 after installation and before final room turnover.

| RECORD | FINDING | DATE AND SOURCE |
| --- | --- | --- |
| Installation | Wall unit, line-set cover, circuit, disconnect, condensate, and seals present | 14 Aug ¦ CES field photo |
| Functional test | Heating, cooling, controls, defrost, and condensate checks passed | 15 Aug ¦ startup sheet |
| Government use | Unit placed in service and used for Office 214 environmental control | Since 16 Aug ¦ facility log |
| Technical inspection | Installed work is acceptable and may remain in place | 18 Aug ¦ CES Mechanical Systems |

Record conclusion The Government received and continues to use a technically acceptable system. This record establishes benefit and condition; it does not decide authority, liability, price reasonableness, or ratification.

/s/ HAL EMMERICH
Hal Emmerich
Mechanical Engineer, 713 CES
18 August 2027