DEPARTMENT OF THE AIR FORCE

SHADOW MOSES AIR FIELD, ALASKA

# AWARDED DESIGN EXTRACT

Task Order FA-27-005 | Campbell Hall Office 214

| Drawing | M-214 Level 2 Mechanical Plan Office 214 |
| --- | --- |
| Issued | 14 February 2027 for construction |
| Task-order value | $26.40 million firm fixed price |
| Design basis | Office 214 served by AHU-2 and terminal unit VAV-2-14 |

The awarded mechanical plan shows two central-system supply diffusers and one return grille serving Office 214 through VAV-2-14. It does not show a wall-mounted indoor unit, outdoor condensing unit, dedicated refrigerant lines, condensate route, disconnect, or separate electrical circuit.

SCOPE AND EQUIPMENT CROSS CHECK

Awarded records for Office 214

## Awarded task-order scope

CLIN 0001 includes phased Campbell Hall renovation, central air-handling and terminal-unit renewal, duct distribution, controls, electrical distribution, interior finishes, and commissioning. Office 214 is an administrative office served by AHU-2 and VAV-2-14. Added permanent equipment must appear in the issued design, equipment schedule, specifications, or an authorized written modification.

| RECORD | AWARDED CONTENT | CROSS CHECK |
| --- | --- | --- |
| M-214 | AHU-2 and VAV-2-14 distribution | No dedicated split system |
| M-601 | Mechanical equipment schedule | No Office 214 split-system equipment |
| E-214 | Level 2 power plan | No dedicated circuit or outdoor-unit feed |
| 23 81 26 | Split-system specification where scheduled | Office 214 is not scheduled |
| Modifications 0001-0004 | Abatement, phasing, and unrelated changes | No Office 214 mini-split addition |

Scope conclusion The installed unit invoiced in IB-01 was outside the awarded work. No Contracting Officer modification added it before performance.

/s/ EMMA EMMERICH
Emma Emmerich
Major, USAF | Contracting Officer, 713 CONS
18 August 2027