DEPARTMENT OF THE AIR FORCE

SHADOW MOSES AIR FIELD, ALASKA

# BENEFIT ACCEPTANCE PRICE AND FUNDS RECORD

Campbell Hall Office 214

| System | One cold-climate ductless heat-pump mini-split serving Office 214 |
| --- | --- |
| Invoice | IB-01 ¦ PW-FA27-005-EXW-001 ¦ $32,000 |
| Inspected | 18 August 2027 by 713 CES Mechanical Systems |
| Condition | Installed, tested, operational, and retained in Government use |

## Technical inspection and benefit

| CHECK | RESULT | EVIDENCE |
| --- | --- | --- |
| Equipment and capacity | Acceptable | Cold-climate rating, design load, and equipment data verified |
| Electrical installation | Acceptable | Circuit, disconnect, labeling, grounding, and testing complete |
| Mechanical installation | Acceptable | Line set, insulation, condensate, penetration, and seals complete |
| Startup and controls | Acceptable | Functional test passed; temperature and defrost controls operate |
| Government use | Confirmed | Office 214 has used the system continuously since 16 August |

RFO FAR 1.405(c)(1) finding The Government accepted and continues to use the benefit of a technically acceptable system. Benefit alone does not authorize payment or cure the authority defect.

## Price analysis

| ELEMENT | INVOICE | GOVERNMENT BENCHMARK | ANALYSIS |
| --- | --- | --- | --- |
| Equipment | $13,680 | $14,050 | Localized supplier catalog and freight |
| Electrical | $5,420 | $5,600 | Quantity takeoff and regional labor |
| Mechanical | $3,260 | $3,390 | Quantity takeoff and regional labor |
| Field labor | $8,360 | $8,588 | 76 hours at $113 benchmark |
| Closeout | $1,280 | $1,300 | Startup, testing, cleanup, and turnover |
| TOTAL | $32,000 | $32,928 | Invoice is 2.8 percent below benchmark |

PRICE DETERMINATION AND FUNDS RECORD

RFO FAR 1.405(c)(4) and (6)

## Contracting Officer price determination

I compared the segregated invoice, supplier purchase records, timecards, regional labor and freight data, and the Government quantity takeoff. The $32,000 invoice is 2.8 percent below the $32,928 benchmark. I found no duplicate cost, unsupported contingency, or cost already paid under the task order. I determine $32,000 fair and reasonable for ratification purposes.

/s/ EMMA EMMERICH
Emma Emmerich
Major, USAF | Contracting Officer, 713 CONS
20 August 2027

## Funds availability certification

| TEST | RECORD | RESULT |
| --- | --- | --- |
| Purpose | FY24 Military Construction, Air Force, Project SM-24-001 Campbell Hall | Appropriate project funds |
| At commitment | Unobligated balance on 11 August 2027 was $418,600 | $32,000 was available |
| At ratification | Unobligated balance reserved on 20 August 2027 was $386,600 | $32,000 remains available |
| Amount | Accounting classification 57 3300 24 713 3010 SM-24-001 | Full amount certified |

Funds certification Appropriate funds existed when Raiden made the commitment and remain available now. No funds are obligated by this certification before ratification approval and the proper contract action.

/s/ ROSEMARY MARQUEZ
Rosemary Marquez
Captain, USAF | Certifying Official, 713 CPTS
20 August 2027