EXERCISE USE ONLY
DEPARTMENT OF THE AIR FORCE
SHADOW MOSES AIR FIELD, ALASKA
AWARDED DESIGN EXTRACT
Task Order FA-27-005 | Campbell Hall Phased Headquarters Renovation
	Drawing
	M-214 — Level 2 Mechanical Plan, Office 214

	Design status
	Issued for Construction — 10 March 2027

	Contractor
	Peace Walker Infrastructure Partners, LLC

	Purpose
	Identify the mechanical work included in the awarded task order


[image: ]
	DRAWING CONTROL: This is an extract of the Government-issued, awarded design. It depicts Office 214 served by the building's central system through VAV-2-14. Interpret it together with the equipment schedule and scope extract on page 2.




SCOPE AND EQUIPMENT CROSS-CHECK
Awarded records for Office 214
Task-order scope extract
CLIN 0001 requires phased renovation of Campbell Hall, including renewal of central air-handling equipment, terminal units, duct distribution, controls, electrical distribution, interior finishes, and commissioning. Office 214 is shown as an ordinary administrative office served by AHU-2 and VAV-2-14. New equipment must appear in the issued drawings, specifications, equipment schedule, or an authorized written modification.
	TAG
	AWARDED EQUIPMENT
	AREA SERVED
	DRAWING / SPEC

	AHU-2
	Central air-handling unit
	Campbell Hall Level 2
	M-201 / 23 73 00

	VAV-2-14
	Variable-air-volume terminal unit
	Office 214 and adjacent zone
	M-214 / 23 36 00

	EF-2-3
	Restroom exhaust fan
	Level 2 restrooms
	M-214 / 23 34 23

	CU-1
	Telecommunications-room cooling unit
	Room 208 only
	M-208 / 23 81 26


Drawing and specification index
	RECORD
	DESCRIPTION
	OFFICE 214 RESULT

	M-214
	Level 2 mechanical plan
	Central supply and return through VAV-2-14

	M-601
	Mechanical equipment schedule
	No dedicated split-system equipment scheduled for Office 214

	E-214
	Level 2 power plan
	No dedicated circuit, disconnect, or outdoor-unit feed for Office 214

	23 81 26
	Split-system air-conditioning specification
	Applies only where equipment is scheduled; Office 214 is not listed


	CONTRACT-FILE FINDING: The awarded task order contains no dedicated mini-split for Office 214. The installed system invoiced in IG-01 is therefore extra-contractual work unless a Contracting Officer later authorized it by written modification. No such pre-installation modification exists in the file.


/s/ HAL EMMERICH
Hal Emmerich
Chief Facilities Engineer, 713 CES
18 August 2027
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